# Engraving cell — intake sheet

Every reading the digital twin still needs from the real machine. Ordered as a route: control panel first, then the cell, then run it. Write in pen; blanks are fine — an honest blank stays tagged as an assumption, a guess becomes a wrong number nobody catches.

| Date | Taken by | Machine / cell |
| --- | --- | --- |
|  |  | Laser engraving cell — Siemens S7, 192.168.0.102, DB59 (158 tags) |

Already answered — do not re-measure. Cell scale and footprint (1614 × 1449.9 mm), workpiece 100 × 100 × 40 mm (100 × 100 from Box_50MM.STEP, 40 mm measured in the lab), magazine capacity (30, six per column across five slots), receiver pressure at cycle start (4.3 bar), sensor type (capacitive), that engraving ends when an operator presses a button, and — new since 2026-08-30 — the role of every solenoid and every proximity sensor, decoded straight from the PLC's own program. This sheet only asks for what the program can't say: where things are bolted, and which physical barrel is which.

Write millimetres, not centimetres. Every length on this sheet is in mm. The last set of lab readings was taken in cm and entered into mm columns — the conveyor as 76 where the tape read 760 mm — and the workbook turned that into a workpiece mass of 0.300 grams instead of 0.300 kg. A full re-baseline was built on it before the error surfaced. Physics_Framework.xlsx now flags out-of-range entries, but this sheet cannot.

Reading the “model assumes” column. That is what the simulation currently believes. Where your reading differs, the model is wrong — which is the point of the sheet. Differences are expected in section C especially.

A · Confirm four solenoids, and cylinder A / B   Blocks structural work

All 13 solenoid roles are now known from the PLC program (decoded 2026-08-30) — printed below for reference, do not re-derive them. Four are still PROVISIONAL because the program names the network, not the physical mechanism: energise each and write down what actually moves. Separately, solenoids 7/8 and 9/10 are confirmed as extend/retract coil pairs on two double-solenoid cylinders — energise %Q3.6 (cylinder A extend) and %Q2.5 (cylinder B extend) one at a time and note which rod belongs to which.

PLC tag → role (known) → what it drives (confirm the four marked)

| Address | PLC tag | Role, from the program | What actually moves |
| --- | --- | --- | --- |
| %Q3.1 | Solenoid_valve1 | magazine compartment 1 pusher | — known — |
| %Q3.0 | Solenoid_valve2 | magazine compartment 2 pusher | — known — |
| %Q2.7 | Solenoid_valve3 | magazine compartment 3 pusher | — known — |
| %Q2.6 | Solenoid_valve4 | magazine compartment 4 pusher | — known — |
| %Q2.2 | Solenoid_valve5 | magazine compartment 5 pusher | — known — |
| %Q0.2 | Solenoid_valve6 | conveyor 1 → 2 transfer (role inferred) | [REC] Energises 2.1 s after conveyor 1 stops on prox 6, together with conveyor 2 ON; drops the instant prox 7 trips. Behaves exactly like the conveyor 1→2 transfer. Still needs an eye on the rod. |
| %Q3.6 | Solenoid_valve7 | cylinder A — extend | — known — |
| %Q2.0 | Solenoid_valve8 | cylinder A — retract | — known — |
| %Q2.5 | Solenoid_valve9 | cylinder B — extend | — known — |
| %Q2.4 | Solenoid_valve10 | cylinder B — retract | — known — |
| %Q2.3 | Solenoid_valve11 | conveyor 2 → 3 transfer (role inferred) | [REC] NEVER energised in any of the five recorded real cycles. The engrave→conveyor 3 move was done by cylinder B (SV9/SV10) instead. It only fires in simulator runs. Energise %Q2.3 by hand. |
| %Q0.1 | Solenoid_valve12 | outfeed, after prox 9 (role inferred) | [REC] Fires on prox 9 for 4.94 s (the T#5S pulse) at the moment the cycle completes — the outfeed that ended every recorded cycle. What it physically pushes is still unseen. |
| %Q2.1 | Solenoid_valve13 | outfeed, after prox 10 (role inferred) | [REC] NEVER energised in any recorded real cycle — prox 10 never tripped either. Energise %Q2.1 by hand to find it. |

Cylinder identity — which barrel is A, which is B

| Energise | Rod that extends | That barrel is cylinder |
| --- | --- | --- |
| %Q3.6 (Solenoid_valve7) |  |  |
| %Q2.5 (Solenoid_valve9) |  |  |

While you're at the panel: are cylinders A and B genuinely double-solenoid valve bodies — a coil at each end, no spring? Four coils driving two rods only makes sense that way, but look and confirm.

B · The ten proximity sensors   Blocks structural work

All ten are now in the model (2026-09-02), in the machine's own numbering, and all ten fire in simulation. Type is settled — they are capacitive — and the roles came from the PLC program (printed below). What is still unknown is where the other four sit — 6, 8, 9, 10 — and the distance at which a real 100 × 100 mm block trips any of them, which the program cannot say for any sensor. One oddity to resolve while you are there: 125 mm is recorded as the rated range, which does not sit comfortably with the M18 capacitive barrel in the CAD — those typically range a few mm to about 20.

Location (confirm four), and trip distance (all ten)

| Address | PLC tag | Role, from the program | Where it is (if not known) | Trip distance |
| --- | --- | --- | --- | --- |
| %I0.3 | Proximity_sensor1 | compartment 1 dispense confirm | — known — |  |
| %I0.7 | Proximity_sensor2 | compartment 2 dispense confirm | — known — |  |
| %I0.0 | Proximity_sensor3 | compartment 3 dispense confirm | — known — |  |
| %I0.1 | Proximity_sensor4 | compartment 4 dispense confirm | — known — |  |
| %I1.1 | Proximity_sensor5 | compartment 5 dispense confirm | — known — |  |
| %I1.5 | Proximity_sensor6 | on conveyor 1 (role inferred) | [REC] Trips 4.77 s after conveyor 1 starts, and conveyor 1 stops on it in the same scan → at or very near the END of conveyor 1. Pace out the mm. |  |
| %I0.4 | Proximity_sensor7 | “WP IN CV2 MID” — conveyor 2 mid | — known — |  |
| %I0.6 | Proximity_sensor8 | end of conveyor 2 (role inferred) | [REC] Never tripped in the fully-watched cycle. The part reached the platform via prox 7 and cylinder A, so FC6 N5 did not run. Position unknown — and worth checking it is not dead or mis-set. |  |
| %I0.2 | Proximity_sensor9 | conveyor 3, gates outfeed (role inferred) | [REC] Trips 1.02 s after conveyor 3 starts and immediately gates the outfeed → near the START of conveyor 3, not the far end. |  |
| %I0.5 | Proximity_sensor10 | conveyor 3, gates outfeed (role inferred) | [REC] Never tripped in any recorded cycle, and SV13 never fired with it. Location unknown. |  |

Sensors 11 and 12 are already accounted for — they are the engraving platform's upper and lower limit switches (%I1.0, %I1.2), not extra proximity sensors. Trip distance in mm, measured by walking a block toward the face until the output changes. If a barrel carries a part number, write it down — it settles the rated-range question outright.

C · Cylinder bores   Blocks structural work

Read the label printed on each barrel. The CAD shows this cell contains two very different cylinders — bore 8 mm with a 4 mm rod, and bore 32 mm with a 12 mm rod (the bore-32 reading is now doubly confirmed: the geometry and the vendor's own part names) — while the model assumes bore 20 throughout, which matches neither. Force goes as bore squared, so the gap between those two is 16×. The PLC program now says there are only two sequencer-driven cylinders, A and B (section A identifies which barrel is which) — plus five magazine pushers and four transfer/outfeed actuators whose mechanism is not yet known. Read the label on whichever of those you can reach.

Per actuator — bore, stroke, and the part number if it is printed

| Which one | Does what | Model assumes | Bore | Stroke | Part number on barrel |
| --- | --- | --- | --- | --- | --- |
| Cylinder A | from section A — extend/retract, station unknown | ⌀ 20 / rod 8 | [CAD] one of ⌀32/rod 12 or ⌀8/rod 4 — nothing in this cell is ⌀20 |  | [CAD] expect 1202510000 (⌀32, folders A27/A28) or 1501160000 (⌀8, folders A51/A52). The model's A53/A54 appears nowhere in the CAD. |
| Cylinder B | from section A — extend/retract, station unknown | ⌀ 20 / rod 8 | [CAD] as cylinder A — ⌀32 or ⌀8 |  | [CAD] same two candidates. [PHOTO] barrels are Janatics, labels legible only as 'MAX PR. 10 bar' and 'MAGNETIC'; model number begins A6. |
| Magazine pusher | any one of the five, solenoids 1–5 | not modelled separately | [CAD] candidate ⌀8 / rod 4 (the small barrel) — a pusher is the plausible home for it, but that is an inference. Read the label. |  |  |
| — press — | Engraving base, vertical (jogged, not a cylinder) | electric axis |  | [PGM] not a stroke: Axis_1 is JOGGED at velocity 72.0 until a limit switch trips (%I1.0 upper, %I1.2 lower). [REC] the two limit inputs are 7.7–8.3 s apart in every recorded cycle, in both directions — that is the travel time, whatever the switch polarity. |  |

Bore and stroke in mm. The CAD part numbers to expect are 1501160000 (the small barrel) and 1202510000 (the large one); the assembly folders name them A51, A52 and A27, A28, and the large one's own Parasolid parts are labelled ⌀32 FEC / ⌀32 REC. If a barrel reads something else entirely, that is worth knowing — the model's own record currently claims A53/A54, which appears nowhere in the CAD.

D · With a stopwatch   Largest single error

Three durations are pure invention, and together they are 12.5 s of a 31.08 s cycle. Because a person paces them, one reading is not enough — take five to ten cycles so the spread is visible. The spread is the real result here: it is what turns a single predicted cycle time into an honest range.

Seconds, one column per cycle

| Interval | Assumed | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Operator notice — part arrives → operator reacts | 3.0 s |  |  |  |  |  |  |  |  |
| Engraving — start → operator's button press | 8.0 s | 28.7 * | 6.0 | 8.8 | 7.3 | 17.5 |  |  |  |
| Operator confirm — button press → machine resumes | 1.5 s | 1.3 * |  |  |  |  |  |  |  |
| Whole cycle, start → part in bin | 31.08 s | 90.0 | 68.9 | 72.1 | 70.5 | 79.7 |  |  |  |

Does the engraving duration depend on the 25 mm / 50 mm product setting? If so, note which product was running — those two figures are engraving lengths, and a longer engrave should take longer. Neither matches the 40 mm block measured in the lab — see section G.

E · Gauges and instruments   Numerical fidelity

Read once, with the machine in its normal running state

| Reading | Model assumes | Actual | Note / how read |
| --- | --- | --- | --- |
| Regulator setting, branch 1 (bar) | 5.5 |  | [PLC] the controller reads no per-branch pressure — only one common supply transmitter (0–10 bar gauge, FC8 N1). Read the four regulator faces by eye. |
| Regulator setting, branch 2 (bar) | 5.5 |  | [PLC] as branch 1 — nothing in the PLC to read. |
| Regulator setting, branch 3 (bar) | 5.5 |  | [PLC] as branch 1 — nothing in the PLC to read. |
| Regulator setting, branch 4 (bar) | 5.5 |  | [PLC] as branch 1 — nothing in the PLC to read. |
| Compressor cut-in / cut-out (bar) | 6.0 / 8.0 |  | [REC/PLC] supply never rose above 4.380 bar in any recording and dipped to 4.03 bar on actuation; live now 4.379 bar. No 6/8 bar sawtooth anywhere. Alarm limits in the PLC are 1.0 / 5.0 bar. Read the switch dial for the real settings. |
| Belt speed setpoint on the drive (m/s) | 0.150 | [PLC] axis Set_Velocity = 180.0 on all three, unit not stated; HighSpeed_Velocity and LowSpeed_Velocity are also 180.0 | 0.150 m/s is a model assumption with nothing behind it. The drive parameter is the 180.0 above, in whatever unit the technology object uses. |
| Belt speed measured — time a mark over a known run (m/s) | 0.150 |  | [REC] belt run times, if you would rather back the speed out of them: conveyor 1 4.77 s to prox 6, conveyor 2 3.15 s (prox 7 at 2.62 s), conveyor 3 1.02 s to prox 9. |
| PLC scan time, as the engineering software reports it (ms) | 10 |  | not in DB59. TIA Portal → the CPU → Online & diagnostics → Cycle time. |
| Are outputs written at end-of-scan, or immediately? | end-of-scan |  | not in DB59. TIA Portal → CPU properties → cycle / I/O update. |
| Sensor trip distance against the real target (mm) | 30 |  | no substitute for the block-and-tape measurement. Nothing in the program or the recording gives a distance. |
| Conveyor position feedback — what unit is it in? | unknown | [PLC] it is NOT a stuck default. Conv1 reads 25.0 right now and swept 2.0 → 25.0 during a cycle; Conv2 1.8 → 30.0; Conv3 2.0 → 30.15. Set_Position: Conv1 25.0, Conv2/3 30.0. HighSpeed_Position: Conv1 30.0, Conv2/3 150.0. All three Axis_Homed_Fb = true. | unit still unknown — the P1 / P2 / tape test is the only thing that settles it. |

The last row refers to Current_Position_Fb, which reads 30.0 in the PLC snapshot with no unit attached. Millimetres, encoder counts and percent are all plausible and they are not interchangeable.

F · One block on a scale   Cheapest open input

Every dimension of the workpiece is now read from the CAD. Density is the one part never confirmed — 750 kg/m³ arrived attached to a measurement that turned out to be wrong, and nothing has checked it since. It scales the mass directly, so it scales every friction and inertia term in the model. Any kitchen scale settles it.

| Reading | Model assumes | Actual | Note |
| --- | --- | --- | --- |
| Mass of one 100 × 100 × 40 mm block (g) | 300 | [MEAS] 300 g | weighed 2026-08-26; 0.300 / (0.1 × 0.1 × 0.04) = 750 kg/m³ exactly. Re-weigh only if the block now on the machine is not that one. |
| Which thickness was on the machine (mm) | 40 | [MEAS] 40 mm | the bench block. The recipe's 50 / 25 mm are engraving LENGTHS, not thicknesses. |
| Wood species, if anyone knows it | — |  | [PHOTO] dark brown hardwood, species unrecorded. Density is already settled by the weighing, so this is nice-to-have, not blocking. |

300 g confirms the assumed 750 kg/m³ exactly. Anything else corrects it in one reading — divide the mass in kg by 0.0004 m³.

G · Running on assumptions — confirm or correct   Updated 2026-09-02

Everything below is already in the model, running, with the value shown. Nothing here blocks work any more — the model proceeds on these and the suites are green. What each row buys is the difference between a number that runs and a number that is true. Correct any that is wrong; leave the rest.

The assumption the model is running on, and what would settle it

| What | Running on | Actual | How to settle it |
| --- | --- | --- | --- |
| Where prox 6 sits along conveyor 1 | near the belt end | [REC] confirmed in kind: conveyor 1 stops on prox 6 in the same scan it trips | pace out the mm from the belt end |
| Where prox 7 sits along conveyor 2 | belt midpoint | [REC] trips 2.62 s into a 3.15 s conveyor-2 run, and conveyor 2 stops 0.53 s later → nearer the end than the midpoint, despite the network title | tape along conveyor 2 |
| Where prox 8 sits along conveyor 2 | belt end | [REC] never tripped in the fully-watched cycle — 'belt end' is unconfirmed and the sensor may not be in the path at all | walk the belt; if it is bolted there, roll a block past it and watch %I0.6 |
| Where prox 10 sits along conveyor 3 | 60% along | [REC] never tripped; SV13 never fired. 60% along is still invention | stand at conveyor 3 and look for a second station |
| Magazine slot pitch (sets prox 1–5 spacing) | 110 mm | [CAD] Magazine.STEP: four 5 mm dividers → five slots of 105–110 mm, 115 deep, 305 tall | one tape measure across the five slots settles which end of 105–110 it is |
| Which compartment the cell feeds from | 1 | [REC] compartment 1 — SV1 fired and prox 1 confirmed the dispense in every real cycle. [PLC] all five compartments read Ok right now | confirmed; change only if the cell is re-set to another compartment |
| Which barrel is cylinder A / B | unassigned | still unassigned — this is the section A panel test | energise %Q3.6, then %Q2.5, and write down which rod moved |
| Cylinder bore | ⌀20 (CAD says 8 and 32) | [CAD] the cell holds ⌀8 (rod 4) and ⌀32 (rod 12). Nothing in it is ⌀20 | read the two body stamps; that also settles which is A and which is B |
| PRODUCT_HEIGHT per compartment | 50 / 25 mm | [PLC] the batch selection reads qty_50mm = 1, qty_25mm = 0 → the cell is currently set up for the 50 mm product, and every recorded real cycle counted one | per-compartment PRODUCT_HEIGHT is not in DB59 — read it on the HMI |
| Conveyor motor | generic 3-phase | [PLC] the three axes are Stepper Technology Objects (tag descriptions), and the owner says the belts are driven by electric motors — so not a generic 3-phase induction drive | one photograph of the drive nameplate settles inertia, torque, gear ratio and speed together |
| Wood species of the blocks | 750 kg/m³, species unknown | [PHOTO] dark brown hardwood; 750 kg/m³ is weighed, not assumed | ask whoever buys the blocks |
| PLC scan time | 10 ms, latency 0 scans | not readable from DB59 | TIA Portal → Online & diagnostics → Cycle time; and CPU properties for the I/O update mode |
| Sensor trip distance vs a real block | 30 mm | unmeasured — no source in the project carries it | walk a real 100 × 100 mm block at one barrel until the output changes |

Two rows are worth more than the rest. The bore scales every pneumatic force by its square — the CAD shows 8 mm and 32 mm in this cell and the model runs 20, which matches neither, so it is wrong by somewhere between 2.6× and 6.2×. The motor is the only unmeasured item in a whole subsystem: belt speed, ramp, gearbox and rotor inertia are all assumed together, so one nameplate settles four numbers at once.

H · Three questions, one look each   From the PLC program

| Question | What the evidence says | Answer |
| --- | --- | --- |
| What is physically loaded in each of the 5 compartments? | program is set for 50 mm and 25 mm; the bench block is 40 mm | [PLC] all five compartments read Ok (none Low, none Empty) at 13:50 on 2026-09-07; the 2026-08-24 snapshot had 1 / 3 / 6 / 3 / 0. Every recorded real cycle drew from compartment 1 and counted a 50 mm product. What is physically stacked in 2–5 still needs eyes. |
| What do the three Pot_Control Conv1/2/3 axes drive? | position axes, separate from the 3 on/off conveyor coils | [PLC] Conv1 Set_Position 25.0, Conv2/3 30.0; HighSpeed_Position 30.0 / 150.0 / 150.0; every velocity 180.0; all three Axis_Homed_Fb true. The feedback tracks real motion — Conv1 swept 2.0 → 25.0 during a cycle — so they are driving something. WHAT they drive is still the question. |
| Do cylinders A and B have position switches fitted? | barrels read MAGNETIC, so they can take them — but the PLC reads none | [PLC] No. The whole 158-tag register carries no cylinder position input: 10 proximity sensors, 2 platform limits, 1 E-Stop. The finding stands — two reed switches would make cylinder A observable. |

The last one is a finding worth passing on to whoever owns the cell, not just to the model. The barrel labels read MAGNETIC, which means the pistons are built to be sensed — yet the PLC latches its own commands (pgm_cylA_Ext) instead of reading a switch. Two reed switches would make cylinder A genuinely observable. That is a wiring choice, not a hardware limit.

Do this FIRST, before anything else — it takes one command

- Widen the recorder, then run the cell ten times from the magazine. At the SCADA machine: python Project_Notes/tools/widen_scada_watch.py --apply, with the backend up and connected. Then run ten or more full cycles starting at the magazine, both products if you can.

Why this is above everything else on this sheet. The only recording this project has of the real cell captured 13 of the machine's 158 tags — solenoids 1–5, conveyors 1 and 3 and all ten proximity sensors were never watched. The model's machine time is 18.580 s and the cell recorded 18.146 and 17.732 s, within 5% — but nobody can yet say whether those were whole cycles, because no pusher was being watched. This one capture answers it. Bring it back with python Project_Notes/tools/read_scada_history.py.

The watch list is held in memory: re-run the script after any restart. It changes only what is recorded and writes no PLC tag.

If you only have ten minutes after that

- Section A, the cylinder A/B rows. Two coils, two rods — five minutes at the panel identifies both barrels for section C.

- Section C, the bore column. Every pneumatic force in the model is derived from a bore that exists nowhere in the cell — the CAD shows 8 mm and 32 mm, and the model runs 20, which matches neither.

- The conveyor motor nameplate (section G). One label settles four assumed numbers at once: belt speed, ramp, gearbox ratio and rotor inertia are all assumed together.

Engraving cell intake sheet · from INPUTS_REQUIRED.md, updated 2026-09-06 — PLC listing, photographs, all ten sensors modelled, trace re-audited	Sheet ___ of ___

Pre-filled 2026-09-07 — what the blue entries above are, and what is left

Everything in blue italic was taken from evidence this project already holds. None of it was read at the machine today, and none of it is a substitute for the pen. Tags: [PLC] read live off the controller at 13:50 on 2026-09-07 through the SCADA backend; [REC] derived from the SCADA recorder's real cycles; [CAD] vendor STEP geometry; [PGM] the TIA Portal listing; [MEAS] weighed or measured in the lab; [PHOTO] read off a photograph of the running cell.

Section D — which cycle each column is

Columns 1–5 are the five real cycles the recorder has, all of them the 50 mm product: 1 = 09-01 18:02, 2 and 3 = the two products in the 09-03 14:39 run, 4 = 09-03 14:44, 5 = 09-07 13:47. Row 2 is the platform's dwell at the top — upper limit switch on to upper limit switch off — which is operator notice plus engraving plus confirm together, because no watched signal separates them. The two starred figures are from the one cycle where Engraving_Completed was actually watched: 27.4 s from the platform reaching the top to the operator's press, then 1.3 s more before the platform moved. Sampling was 1 Hz, so read these to ±1 s. A stopwatch over ten cycles still beats them, and it is the only way to split notice from engrave.

The number worth arguing about

Subtract the operator dwell from each recorded cycle and the machine time is 61.3, 63.0, 63.4, 63.2 and 62.2 s — a spread of two seconds across five cycles on three different days. The model's machine time is 18.58 s. Whatever else this sheet settles, that gap is three and a half times and it is not operator variance.

And one correction to carry back

The 18.146 s and 17.732 s cycles this project records as the real cell are not the cell. Both ran while the backend's connection state was SIMULATED — the built-in PLC stand-in — and it shows: pressure pinned at exactly 6.2 bar, belt velocities of exactly 0.150 and 0.200 m/s (the model's own parameters), and not one proximity sensor or magazine pusher transition in either cycle. The real cycles read 4.0–4.4 bar and run 69–90 s. The agreement 'within 5%' was the model agreeing with itself.

What is still missing, and how to get it

1. Which barrel is cylinder A, which is B — energise %Q3.6, then %Q2.5, one at a time from the manual-command page, and watch which rod extends. Two coils, two answers, five minutes. Also look at the two valve bodies while you are there: a coil at each end and no spring means double-solenoid, which is what the model now assumes.

2. The bore stamps — read the label on cylinder A, on cylinder B, and on any one magazine pusher you can reach. Expect 1202510000 (⌀32) or 1501160000 (⌀8). Photograph each stamp; a wrong transcription here is worth 16× in force.

3. The four unseen solenoids — energise %Q0.2, %Q2.3, %Q0.1 and %Q2.1 one at a time and note what each moves. %Q2.3 and %Q2.1 matter most: neither has ever fired in a recorded cycle, so nothing in the data says where they are or whether they work.

4. Where prox 6, 8, 9 and 10 are bolted — walk the cell with the address list and pace each one from the near end of its belt, in mm. Prox 8 and 10 have never tripped in a recording, so check they are in the path at all.

5. Trip distance, all ten — walk a real 100 × 100 mm block toward each face until the output changes, and read the gap in mm. If any barrel carries a part number, write it down: it settles the 125 mm rated-range oddity outright.

6. The stopwatch, five to ten cycles — operator notice, engrave, confirm, whole cycle, both products if you can. The recorder gives their sum; only a stopwatch splits it. Note which product was running each time.

7. The four regulator faces and the compressor switch dial — the PLC reads one common supply transmitter and nothing per branch, so these are eyes-only. Read them with the machine in its normal running state.

8. Belt speed, measured — put a mark on the belt and time it over a known distance. That one number turns every run time in this sheet into a position in mm.

9. The conveyor position unit — mark the belt, note Conv1.Current_Position_Fb as P1, run the belt, note P2, and tape-measure the millimetres the mark travelled. One unit = mm ÷ (P2 − P1). The feedback does move, so the test will work.

10. The conveyor drive nameplate — one photograph settles rotor inertia, torque limit, gear ratio and belt speed together. It is the only wholly unmeasured subsystem left.

11. PLC scan time and I/O update mode — TIA Portal reports both directly; neither is in DB59.

12. Per-compartment PRODUCT_HEIGHT and what is physically stacked in each — the HMI has the recipe; only your eyes have the stack.

13. Does the platform hold or fall when its drive is disabled — press the E-Stop with the platform raised and watch. The model refuses to guess either way.